VENTIS

Mathematical & Numerical Reference

Every equation, constant, range and threshold in one place — stated in the simplest form that is still correct

| Field | Value |
| --- | --- |
| Document ID | AQR-MATH-001 · Revision v1.0 · 2026-09-05 |
| Companion documents | AQR-ARCH-001 (PRD / Architecture), AQR-DATA-001 (Dataset Specification) |
| Applies to | VENTIS closed-loop air-quality remediation controller, 250 mm demonstration chamber |
| How to use | Each equation has an ID (E1, E2 …). Numbers live in Section 11. If a number appears in both, Section 11 wins. |

Conventions used throughout

- Time t is in seconds unless a symbol carries an _hr suffix, which means per hour.

- Concentration C is micrograms per cubic metre for particulate matter and parts per million for CO2.

- u is the duty cycle, a number between 0 and 1. It is the only thing the controller can change.

- A hat, as in C_hat, means a predicted value. No hat means a measured value.

- exp(x) is the exponential function; ln(x) is the natural logarithm.

- Subscript k counts control steps of 10 seconds each. Subscript i counts 1-second samples.

# Contents

# 1. Symbols

Every symbol used anywhere in the project, with the value it usually takes on the 250 mm demonstration chamber.

| Symbol | Meaning | Unit | Typical value on the demo rig |
| --- | --- | --- | --- |
| C | Pollutant concentration in the chamber | ug/m3 or ppm | 5 to 950 ug/m3 (PM2.5) |
| C0 | Concentration at the moment the source stops | ug/m3 | 60 to 950 |
| C_in | Concentration of the incoming make-up air | ug/m3 or ppm | 0 for PM (HEPA), 400-500 ppm for CO2 |
| C_safe | Concentration counted as safe | ug/m3 | 60 (CPCB satisfactory ceiling) |
| V_eff | Effective air volume of the chamber | m3 | 0.0150 (15.0 L) |
| Q(u) | Volumetric airflow the turbine produces at duty u | m3/h | 0 to about 1.8 |
| lambda(u) | Forced air-exchange rate = Q/V_eff | 1/s | 0 to 0.032 |
| ACH | Air changes per hour = 3600 x lambda | 1/h | 0 to about 115 |
| k_dep | Deposition rate: particles settling on walls | 1/h | 0.8 to 3.0 |
| k_leak | Passive leak rate with the turbine off | 1/h | at most 0.5 |
| k_tot | Total removal rate = lambda + k_dep + k_leak | 1/h or 1/s | 2 to 118 per hour |
| tau_eff | Time constant = 1 / k_tot | s | 31 s at full duty; about 30 min at zero duty |
| u | Commanded duty cycle | - | 0, or 0.25 to 1.00 |
| u_min | Duty below which the motor will not turn | - | 0.25 to 0.30 (measure it) |
| V_bus | Motor supply voltage measured on the rail | V | 11.4 to 12.6 |
| I_motor | Motor current | A | 0 to 0.30 running, up to 0.9 at start |
| S(t) | Source term: pollutant entering the air | ug/s | 0 during decay |
| I_inst | Instantaneous remediation index (the control variable) | index | 0 to 500 |
| I_safe | Index target | index | 100 |
| T_target | Deadline to reach I_safe | s | 90, 150, 300 or 600 |
| T_c | Control interval, how often the optimiser re-plans | s | 10 |
| N | Prediction horizon in control steps | - | 30 (= 300 s) |
| Rs | MQ sensor resistance right now | ohm | 200 to 200000 |
| R0 | MQ sensor resistance in clean air (the baseline) | ohm | measured at commissioning |
| kappa | Hygroscopic growth factor for PM correction | - | 0.25 to 0.50 (start at 0.30) |

# 2. How the air in the chamber behaves

This is the whole physical model. Everything else in the project is built on these six equations.

## 2.1 The mass balance

E1   dC/dt  =  -(lambda(u) + k_dep + k_leak) * C  +  S(t)/V_eff  +  lambda(u) * C_in

In words: Concentration falls at a rate proportional to how much is currently there. The fan sets most of that rate; walls and leaks add a little. The last two terms are the source and whatever comes in through the inlet, and both are zero or near zero during a decay.

E2   k_tot  =  lambda(u) + k_dep + k_leak

In words: One number that bundles every way a particle can leave the air.

## 2.2 The decay curve — the shape of every experiment

E3   C(t)  =  C_in + (C0 - C_in) * exp( -k_tot * t )

In words: Once the source stops, concentration falls along a smooth exponential. Every episode in the dataset is one of these curves.

E4   tau_eff  =  1 / k_tot          63% gone after 1 tau, 86% after 2, 95% after 3

In words: The time constant is the single number that says how fast this chamber cleans itself at a given fan speed.

E5   ACH  =  Q [m3/h] / V_eff [m3]           lambda [1/s] = ACH / 3600

In words: Air changes per hour is the intuitive version of lambda. 115 ACH means the chamber's whole air volume is replaced 115 times an hour.

## 2.3 How to measure k_tot from data

E6   ln( (C - C_in) / (C0 - C_in) )  =  -k_tot * t         (fit a straight line, slope = -k_tot)

In words: Take logs and the exponential becomes a straight line. The slope is the removal rate. You must subtract C_in first — forgetting the 400 ppm of ambient CO2 is the most common mistake in this kind of test.

## 2.4 The three-step identification chain

| Step | Experiment | What it gives you | Why it works |
| --- | --- | --- | --- |
| 1 | CO2 decay, fan OFF | k_leak | CO2 does not stick to walls, so k_dep = 0, and the fan is off, so lambda = 0. Whatever decay you see is the leak. |
| 2 | PM decay, fan OFF | k_dep = (measured slope) - k_leak | Now the only two terms are deposition and leak, and you already know the leak. |
| 3 | CO2 decay at each duty u | lambda(u) = (measured slope) - k_leak, then Q(u) = lambda(u) x V_eff | Again k_dep = 0 for CO2, so the extra decay over step 1 is entirely the fan. |

Do these in this order. Attempted in any other order, the three unknowns are tangled together and none of them can be recovered.

## 2.5 Can the deadline be met?

E7   ACH_required  =  3600 * ln(C0 / C_safe) / T_target  -  (k_dep + k_leak)

In words: How hard the fan must work to get from C0 down to C_safe within the deadline. If this comes out above ACH_max, the deadline is physically impossible and the controller should run flat out and report the miss.

E8   C_best(T)  =  C0 * exp( -(ACH_max/3600 + ...) * T )      lowest reachable concentration in time T

In words: What full duty can achieve. Compare against C_safe to label an episode feasible or not.

Required ACH for the demo chamber (k_dep + k_leak taken as 2.0 per hour). Cells marked IMPOSSIBLE exceed the roughly 115 ACH the 2 W turbine can deliver.

| How dirty (C0 / C_safe) | T = 90 s | T = 150 s | T = 300 s | T = 600 s |
| --- | --- | --- | --- | --- |
| 2x (120 -> 60) | 26 ACH | 15 ACH | 6.8 ACH | 2.7 ACH |
| 5x (300 -> 60) | 63 ACH | 37 ACH | 18 ACH | 8.2 ACH |
| 10x (600 -> 60) | 91 ACH | 54 ACH | 26 ACH | 12 ACH |
| 16x (960 -> 60) | IMPOSSIBLE (137) | 68 ACH | 33 ACH | 16 ACH |

# 3. Fan, motor and energy

## 3.1 Duty cycle to airflow

E9   Q(u)  =  0                     if u < u_min
Q(u)  =  Q_max * phi(u)        if u >= u_min

In words: Below about 25% duty a small brushed motor does not turn at all — that is stiction, and it means the achievable duty set is zero plus a band from u_min up to 1, with a hole in between. phi is a curve you measure, not a formula you assume.

E10   lambda(u)  =  Q(u) / V_eff

In words: This is the bridge between the thing you control and the thing you care about.

phi(u) must be fitted with a monotone-preserving spline (PCHIP). A polynomial fit will wiggle, produce a region where more fan means less airflow, and the optimiser will find that region and command nonsense.

## 3.2 Fan affinity laws

E11   Q  proportional to  N          (airflow scales with speed)
dP proportional to  N^2        (pressure scales with speed squared)
P_shaft proportional to N^3    (power scales with speed CUBED)

In words: This cubic term is the entire economic reason this project exists. Running the fan at half speed for twice as long uses roughly a quarter of the energy, because power grows as the cube of speed while the cleaning job only needs airflow.

## 3.3 Electrical quantities

E12   V_applied  =  u * V_bus  -  V_drop(driver)

In words: Never assume V = u x 12. An L298N loses about 2 V in its output transistors, and the rail sags under load. This is why the bus voltage is measured on GPIO 39.

E13   P_elec  =  V_bus * I_motor              [watts]

E14   E_Wh  =  ( sum over samples of P_elec * dt ) / 3600

In words: True energy in watt-hours. This is the number the energy-saving claim is made on.

E15   J_V2  =  sum over k of ( u_k * V_bus )^2 * dt          [the optimiser's objective]

In words: The optimiser minimises this instead of E_Wh because it is smooth and easy to differentiate. It points the same way but it is not watt-hours, so it is never quoted as the result.

## 3.4 Realising a duty below the stiction threshold

E16   on_fraction  f  =  Q_target / Q(u_min)      run at u_min for f * T_c seconds, then 0 for the rest

In words: The chamber's time constant is 31 seconds and the control interval is 10 seconds, so the air cannot tell the difference between a steady low airflow and a fan that pulses within the interval. It only sees the average.

E17   Kick-start: on any 0 -> non-zero transition, hold u = 1.00 for 400 ms, then drop to target

In words: Breaks stiction. Without it, a command of 0.28 from standstill produces nothing at all.

# 4. Turning sensor readings into numbers you can trust

## 4.1 The MQ gas sensors

E18   Rs  =  R_L * ( V_cc - V_out ) / V_out

In words: Converts the voltage the module puts out into the sensing element's resistance. R_L is the module's on-board load resistor and it varies by up to 30% between units, so measure it.

E19   ratio  r  =  Rs / R0

In words: The only MQ quantity allowed anywhere in this project. A ratio below 1 means more gas than clean air. Datasheet parts-per-million curves are single-gas, dry-air extrapolations and are not used.

E20   V_out  =  ( ADC_counts / 4095 ) * 3.10 V * 1.667        (1.667 = the 10k/15k divider ratio)

E21   R0_new  =  0.98 * R0_old  +  0.02 * Rs_clean            (EWMA, only in certified clean air)

In words: Slowly re-learns the clean-air baseline so that sensor ageing does not look like pollution.

E22   r_corrected  =  r / f(T, RH)

In words: Removes the temperature and humidity response. Without it the model learns that afternoons are polluted, because afternoons are humid.

## 4.2 Particulate matter

E23   C_dry  =  C_measured / ( 1 + kappa * ( RH / (100 - RH) ) )

In words: Particles absorb water and look bigger to a laser. This shrinks them back. Above 90% relative humidity the correction is no longer trustworthy and the reading is marked invalid instead.

## 4.3 Smoothing and rates of change

E24   dC/dt  ~=  ( -2*C[i-2] - C[i-1] + C[i+1] + 2*C[i+2] ) / ( 10 * dt )      (5-point Savitzky-Golay)

In words: A clean way to get a slope from noisy data. A plain difference between two samples is dominated by noise.

E25   EWMA:   y[i]  =  a * x[i]  +  (1 - a) * y[i-1]        with  a = dt / tau_smooth

In words: Exponential smoothing. Three of these run at once with tau of 15 s, 60 s and 300 s, giving the model a fast, a medium and a slow view of the same channel.

E26   k_tot_estimate  =  -3600 * (dC/dt) / (C - C_in)          [per hour]

In words: The live removal rate, straight from the data. Meaningless when C is close to C_in, so it is set to blank below a 20 ug/m3 difference.

# 5. The air-quality index

Regulatory AQI is defined on a 24-hour average, which can never move inside a 15-minute deadline. The project therefore uses two different indices: a fast one for control, and the standard one for reporting.

## 5.1 Sub-index interpolation

E27   SI  =  SI_lo  +  ( SI_hi - SI_lo ) / ( C_hi - C_lo ) * ( C - C_lo )

In words: Straight-line interpolation inside whichever concentration band the reading falls into. SI_lo/SI_hi and C_lo/C_hi come from the tables below.

E28   I_inst  =  max( SI_pm25 , SI_pm10 , SI_gas , SI_co2 )

In words: The worst pollutant sets the index. Which one it was is recorded as the driver channel.

## 5.2 CPCB National AQI breakpoints (default for India)

| Index band | Category | PM2.5 (ug/m3, 24 h) | PM10 (ug/m3, 24 h) | NH3 (ug/m3) |
| --- | --- | --- | --- | --- |
| 0 - 50 | Good | 0 - 30 | 0 - 50 | 0 - 200 |
| 51 - 100 | Satisfactory | 31 - 60 | 51 - 100 | 201 - 400 |
| 101 - 200 | Moderate | 61 - 90 | 101 - 250 | 401 - 800 |
| 201 - 300 | Poor | 91 - 120 | 251 - 350 | 801 - 1200 |
| 301 - 400 | Very Poor | 121 - 250 | 351 - 430 | 1201 - 1800 |
| 401 - 500 | Severe | above 250 | above 430 | above 1800 |

## 5.3 US EPA breakpoints (optional, for international comparison)

| Index band | PM2.5 (ug/m3, 2024 revision) | PM10 (ug/m3, unchanged) |
| --- | --- | --- |
| 0 - 50 | 0.0 - 9.0 | 0 - 54 |
| 51 - 100 | 9.1 - 35.4 | 55 - 154 |
| 101 - 150 | 35.5 - 55.4 | 155 - 254 |
| 151 - 200 | 55.5 - 125.4 | 255 - 354 |
| 201 - 300 | 125.5 - 225.4 | 355 - 424 |
| 301 - 500 | above 225.4 | above 424 |

## 5.4 The two project-defined sub-indices

Neither CO2 nor an uncalibrated gas sensor is an AQI pollutant. These two mappings are invented for this project so that the max operator in E28 is meaningful, and they are labelled as such wherever they are reported.

| CO2 (ppm) | SI_co2 | Basis |
| --- | --- | --- |
| 400 | 0 | clean outdoor air |
| 800 | 50 | ASHRAE comfort guidance |
| 1000 | 100 | common indoor ventilation limit |
| 1500 | 200 | clearly under-ventilated |
| 2500 | 300 | drowsiness, poor air |
| 5000 | 500 | OSHA 8-hour exposure limit |

E29   SI_gas  =  100 * clip( ( R0/Rs - 1 ) / ( k_alarm - 1 ) , 0 , 5 )

In words: Maps the MQ-135 ratio onto the same 0 to 500 scale. k_alarm is set once per site during commissioning. MQ-2 is deliberately NOT in this formula — flammable gas triggers a shutdown, not more ventilation.

## 5.5 NowCast, for reporting only

E30   w  =  max( C_min / C_max , 0.5 )
NowCast  =  sum( w^i * C_i ) / sum( w^i )        over the trailing 12 hourly means

In words: The standard way of turning recent hourly readings into a number comparable with published AQI. It is shown on the dashboard and never used by the controller.

# 6. Features given to the model

| Feature family | Formula | Why it earns its place |
| --- | --- | --- |
| Lags | x(t - k) for k = 1, 5, 10, 30, 60, 120 s | A dynamic system depends on its own past. Tree models cannot see the past unless you hand it to them. |
| First difference | ( x(t) - x(t-h) ) / h for h = 5 s and 30 s | The rate of decay carries the physics; the level alone does not. |
| Second difference | difference of the difference | Distinguishes a steady decay from one that is still accelerating. |
| EWMA | E25 with tau = 15, 60, 300 s | Separates trend from noise at three timescales. |
| Rolling spread | standard deviation over 60 s | Rises when the fan stirs the chamber; a useful state signal. |
| Cumulative exposure | integral of max(I_inst - I_safe, 0) dt since episode start | Turns the deadline into something the model can see. Also the compliance number. |
| Physics feature | lambda(u) = Q(u)/V_eff, and the removal term C * lambda(u) | Handing the model the physics is what lets a tree represent an exponential it could never extrapolate. |
| Baseline difference | x(t) - (5th percentile of x over the trailing 24 h) | Drift-proof: shows the excursion rather than the absolute level. |
| Corrected channels | E22 and E23 | Removes false humidity and temperature signals. |
| Time context | sin and cos of hour-of-day, minutes since episode start, T_target - t_elapsed | Sources and ambient air are diurnal; remaining time is a genuine input to the control problem. |

Two things are forbidden as features: anything computed from the future of the target, and the COMMANDED duty. Only the APPLIED duty may be used, otherwise the model learns the controller instead of the plant.

# 7. The forecasting model

## 7.1 The grey-box structure

E31   C_hat[k+1]  =  C[k]  +  dt * ( -(lambda(u_k) + k_dep + k_leak) * C[k]  +  lambda(u_k) * C_in )   +   g_theta( x_k , u_k )
              |________________ known physics (E1) ________________|       |__ learned residual __|

In words: The physics does the heavy lifting and guarantees the right shape and the right sign everywhere. The machine-learning part only has to correct a 10 to 20 percent error, which is a far easier problem than discovering air-exchange physics from 160 experiments.

## 7.2 NARX — the primary residual model

E32   y[k+1]  =  f( y[k], y[k-1], ..., y[k-ny] ,  u[k], u[k-1], ..., u[k-nu] )

In words: Nonlinear AutoRegressive with eXogenous input. It is a model of a system that moves, which is the honest shape for a system that moves.

E33   h  =  tanh( W1 * x + b1 )          hidden layer, 24 units
y  =  W2 * h + b2                  linear output

E34   parameter count  =  ( n_in + 1 ) * n_h  +  ( n_h + 1 )        e.g. 34 inputs, 24 hidden  ->  865 parameters

In words: Keep it under about 2,000 parameters. With only a few hundred experiments, a bigger network memorises episodes instead of learning dynamics.

E35   Loss  =  mean( ( y - y_hat )^2 )  +  1e-4 * sum( weights^2 )

## 7.3 XGBoost — the fallback and ensemble member

E36   Objective  =  sum of loss( y_i , y_hat_i )  +  sum over trees of [ gamma * T  +  0.5 * lambda_reg * ||w||^2 ]

In words: Standard gradient boosting: fit the errors of the previous trees, and penalise trees for having many leaves (gamma) or large leaf values (lambda_reg).

E37   monotone_constraints:  -1  on duty, on every duty lag, and on lambda(u)

In words: A hard structural promise that more fan can never predict a higher index. Without it, the optimiser finds a flat or wrong-signed region of the tree and parks there. This one line is the cheapest safeguard in the project.

## 7.4 Combining them

E38   y_ensemble  =  ( y_narx / var_narx  +  y_xgb / var_xgb ) / ( 1/var_narx  +  1/var_xgb )

In words: Inverse-variance weighting: whichever model has been more reliable lately counts for more.

E39   disagreement  =  | y_narx - y_xgb |        ->  widen the controller's safety margin when this is large

## 7.5 Predicting further than one step

E40   C_hat[k+1] from C[k];  then C_hat[k+2] from C_hat[k+1];  ... repeat N times

In words: Recursive rollout. Errors compound, which is exactly why the 300-second forecast is allowed a larger error budget than the 60-second one.

# 8. The optimiser

## 8.1 The problem, stated in full

MPC   minimise over u_0 ... u_(N-1):

      
    sum_k ( u_k * V_bus )^2 * dt        <- energy proxy, the thing being saved
  + lambda_slew * sum_k ( u_k - u_(k-1) )^2   <- penalty for changing the fan speed
  + lambda_slack * s^2                        <- penalty for missing the deadline

      
subject to:
    0 <= u_k <= 1                             <- the fan cannot do more than exist
    | u_k - u_(k-1) | <= 0.10                 <- no violent changes
    I_hat( T_target ) <= I_safe + s ,  s >= 0 <- the deadline, as a SOFT constraint
    u_0 within 0.10 of the duty running now   <- the first move must be reachable

In words: Find the gentlest fan profile that still gets the air clean by the deadline. The deadline is soft — if it is physically impossible, the optimiser runs flat out and reports how far short it will fall, rather than failing to produce any command at all. A live controller must always return something.

## 8.2 Practical settings

| Setting | Value | Reason |
| --- | --- | --- |
| Horizon N | 30 steps of 10 s = 300 s | About 10 time constants ahead; further is guesswork |
| Decision variables after move-blocking | 8 (step pattern 1,1,1,2,2,4,8,11) | Cuts the problem size roughly fourfold; the far end of the horizon is re-planned before it is ever executed |
| Slew limit | 0.10 per control interval | Also enforced independently on the ESP32, so a bad command cannot slam the actuator |
| lambda_slack | 1e4 | Large enough that the deadline is effectively hard whenever it is achievable |
| Warm start | previous solution shifted one step, last value repeated | Typically halves the number of iterations |
| Solver, phase 1 | SciPy SLSQP | No extra dependencies; measured 480 ms at the 95th percentile |
| Solver, phase 2 | CasADi + IPOPT (optionally via do-mpc) | Exact gradients from the small neural network; 5 to 10 times faster |
| Hard time cap | 900 ms | On timeout, publish the best feasible answer so far. Never publish nothing |

# 9. Metrics

## 9.1 Forecast quality

M1   RMSE  =  sqrt( mean( ( y - y_hat )^2 ) )

M2   MAE   =  mean( | y - y_hat | )

M3   sMAPE =  100 * mean( | y - y_hat | / ( ( |y| + |y_hat| ) / 2 ) )

M4   Skill =  1  -  RMSE_model / RMSE_persistence

In words: Skill compares the model against the laziest possible forecast, namely 'it will stay exactly as it is'. A skill of 0 means the model added nothing.

M5   Coverage  =  fraction of true values inside the 90% prediction interval        (should be 0.88 to 0.92)

## 9.2 Controller quality

M6   Energy saving  =  1  -  ( sum of E_Wh with MPC ) / ( sum of E_Wh always-on )

M7   Optimality gap =  E_MPC / E_oracle           (oracle = re-optimised offline with perfect hindsight)

M8   Deadline compliance  =  fraction of episodes with I_inst( T_target ) <= I_safe

M9   Overshoot waste  =  energy spent after the index cleared  /  total episode energy

M10   Chatter  =  mean over control intervals of | u_k - u_(k-1) |

## 9.3 Drift detection

M11   Page-Hinkley:   m_T = sum_(t<=T) ( e_t - mean_e - delta ) ;   PH = m_T - min(m_t)
                alarm when PH > threshold_lambda         delta = 0.005 , threshold_lambda = 12

In words: Watches the forecast error for a persistent shift. It fires on a slow systematic drift, which a simple threshold on error would miss.

M12   PSI  =  sum over bins of ( actual% - expected% ) * ln( actual% / expected% )
        below 0.10 = fine ,  0.10 to 0.25 = watch it ,  above 0.25 = act

In words: Population Stability Index: has the shape of the incoming data moved away from what the model was trained on?

# 10. Every important number, in one table

## 10.1 Chamber and physics

| Quantity | Value | Status |
| --- | --- | --- |
| Chamber internal dimensions | 250 x 250 x 250 mm | fixed |
| Geometric volume V_geom | 15.625 L = 0.015625 m3 | fixed |
| Effective volume V_eff | about 15.0 L (subtract the hardware inside) | MEASURE |
| Surface-to-volume ratio | 24 per metre | fixed |
| Airflow at full duty Q_max | expect 0.6 to 3.0 m3/h; design point 1.8 | MEASURE |
| Air changes per hour at full duty | expect 38 to 192; design point 115 | MEASURE |
| Fastest time constant tau_min | about 31 s at the design point | derived |
| Deposition rate k_dep | expect 0.8 to 3.0 per hour | MEASURE |
| Leak rate k_leak | must be at most 0.5 per hour | MEASURE (acceptance test) |
| Stiction threshold u_min | expect 0.22 to 0.30 | MEASURE |
| Thermal time constant | about 70 minutes | derived |
| Warm-up before any experiment | at least 90 minutes | rule |
| Temperature rise from MQ heaters | about +2.0 C | derived |

## 10.2 Timing

| Quantity | Value | Note |
| --- | --- | --- |
| Sensor sampling rate | 1 Hz | 31 samples per time constant; also the PMS5003's own limit |
| Electrical sampling | 10 Hz internally, reported as 1 s mean and spread | PWM makes current and voltage fast |
| Edge safety loop | every 100 ms | Runs on the ESP32, independent of the network |
| Control interval T_c | 10 s | 16 times the decision latency, one twelfth of the plant time constant |
| Prediction horizon | 300 s (30 steps) |  |
| Command validity window | 30 s (3 control intervals) | After this the node falls back to its own rules |
| Decision latency, 95th percentile | 617 ms | Ceiling is 1.5 s |
| Optimiser solve, 95th percentile | 480 ms | Hard cap 900 ms |
| Actuator settle time | about 250 ms | Measure it; if it exceeds T_c/10, increase T_c |
| Deadline T_target options | 90, 150, 300, 600 s | Rig-specific. The 900 s figure from the PRD does not apply to a 15 L chamber |

## 10.3 Electrical

| Quantity | Value |
| --- | --- |
| Supply | 12 V / 2 A mains SMPS (24 W), plus a 12 V to 5 V buck |
| Sensor and logic rail draw | about 544 mA at 5 V = 2.69 W average, 870 mA peak |
| MQ heater pair | 310 mA, 1.55 W — 58% of the sensor load, and it cannot be duty-cycled |
| PMS5003 | 100 mA running, under 200 uA asleep |
| MH-Z19B | under 20 mA average, 150 mA peak during the lamp pulse |
| Motor at full duty | about 175 mA, 2.1 W; start-up surge about 900 mA for under 300 ms |
| Total system | 5.2 W nominal, 15.8 W transient |
| Battery runtime if attempted | about 12 hours from a 20,000 mAh pack — this is why the design is mains-powered |
| PWM frequency | 20 kHz (above hearing) |
| PWM resolution | 11 bits = 2048 steps |
| Kick-start pulse | 400 ms at full duty |
| Bus voltage valid range | 11.4 to 12.6 V |

## 10.4 Thresholds and limits

| Threshold | Value | What happens when it is crossed |
| --- | --- | --- |
| I_safe | 100 index points | Below it the fan may stop; above it remediation starts |
| C_safe (PM2.5) | 60 ug/m3 | The concentration equivalent of I_safe |
| Index hysteresis | 10 points | Stops the controller flickering around the boundary |
| Index deadband | plus or minus 5 points | No action for changes smaller than this |
| Humidity invalidation | above 90% RH | PM readings marked invalid; index falls back to other channels |
| PM saturation | 950 ug/m3 | Episode rejected; the sensor is no longer trustworthy |
| Minimum usable C0 | 60 ug/m3 | Below this there is nothing to remediate; episode rejected |
| Decay fit quality | r-squared below 0.97 | Episode rejected — it means the chamber was not well mixed |
| Command staleness | 30 s without a valid command | Node switches to its own rule-based ladder |
| Watchdog timeout | 3 s | ESP32 resets; hardware pull-downs hold the motor off |
| Sensor fault | primary channels invalid for 120 s | Node holds a conservative fixed 60% duty and alarms |
| Flammable gas (MQ-2) | site-set, well below the lower explosive limit | MOTOR TO ZERO, alarm, latched until a person acknowledges |
| Chatter alarm | mean duty change above 0.15 over 10 intervals | Slew penalty is doubled automatically |
| R0 drift warning | 10% in 30 days | Investigate |
| R0 drift action | 20% from commissioning | Recalibrate or replace the sensor |
| Performance rollback | deadline compliance below 90% over 50 episodes | Revert to the previous model |

## 10.5 The fallback ladder (runs on the ESP32 with no network)

| Measured index | Duty commanded |
| --- | --- |
| below I_safe - 10 | 0% |
| I_safe - 10 up to I_safe | 30% |
| I_safe up to 1.25 x I_safe | 55% |
| 1.25 to 1.5 x I_safe | 80% |
| above 1.5 x I_safe | 100% |
| MQ-2 flammable threshold breached | 0% plus alarm — overrides everything above |

## 10.6 Success targets

| Metric | Target | Minimum acceptable |
| --- | --- | --- |
| Energy saving versus always-on | 40% | 25% |
| Deadline compliance | 95% | 90% |
| Recovery-time error (90th percentile) | 10% of T_target | 20% |
| Forecast RMSE at 60 s | 3.0 index points | 5.0 |
| Forecast RMSE at 300 s | 8.0 index points | 12.0 |
| False triggers per 72 hours idle | 1 | 3 |
| Missed events above 1.5 x I_safe | 0% | 0% |
| Overshoot waste | 5% of episode energy | 10% |
| Decision latency (95th percentile) | 1.5 s | 2.5 s |
| Telemetry completeness | 99.5% per day | 99.0% |
| Fault-injection tests passed | 10 of 10 | 10 of 10 |

## 10.7 Dataset quantities

| Quantity | Minimum (Tier 1) | Target (Tier 2) |
| --- | --- | --- |
| Episodes | 172 | 430 |
| Rows at 1 Hz | about 179,000 | about 830,000 |
| Effective sample size | 172 | 430 |
| Chamber hours (attended) | 34.6 | 84.7 |
| Storage as Parquet | 6.5 MB | 30 MB |
| Duty levels | 9 (0, 0.25, 0.30, 0.40, 0.50, 0.60, 0.75, 0.90, 1.00) | same |
| Aerosol sources | at least 3 | 4 |
| Concentration bands | 5 (60-120, 120-250, 250-450, 450-700, 700-950 ug/m3) | same |
| Episodes needed before XGBoost may train | 60 | - |
| Episodes needed before NARX may train | 100 | - |
| Train / validation / test split | 70 / 15 / 15 by EPISODE, never by row | same |

The one rule that governs all of the above: any value marked MEASURE is a placeholder until the commissioning procedure has produced a real number for this specific rig. Nothing may be trained, tuned or claimed on an assumed value.